## Line Data
Real Units Calculations
From Bus | To Bus | Rated Voltage (kv) | Sbase (MVA) | Length(km) | R (pu) | X (pu) | B (pu) | Z Base | Y Base | R (ohm) | X (ohm) | B (uS) | Type
1 | 2 | 230 | 100 | 100 | 0.01131 | 0.08998 | 0.18377 | 529 | 0.0018904 | 5.983 | 47.5994 | 347.3913 | L 7-8
1 | 6 | 230 | 100 | 300 | 0.03394 | 0.26995 | 0.5513 | 529 | 0.0018904 | 17.9543 | 142.8036 | 1042.155 | L 4-6
2 | 5 | 230 | 100 | 400 | 0.0453 | 0.3599 | 0.7351 | 529 | 0.0018904 | 23.9637 | 190.3871 | 1389.603 | L 4-5
3 | 4 | 230 | 100 | 100 | 0.01131 | 0.08998 | 0.18377 | 529 | 0.0018904 | 5.983 | 47.5994 | 347.3913 | L 3-4(1)
3 | 4 | 230 | 100 | 100 | 0.01131 | 0.08998 | 0.18377 | 529 | 0.0018904 | 5.983 | 47.5994 | 347.3913 | L 3-4
4 | 5 | 230 | 100 | 150 | 0.017 | 0.135 | 0.2757 | 529 | 0.0018904 | 8.993 | 71.415 | 521.172 | L 2-5
4 | 6 | 230 | 100 | 300 | 0.03394 | 0.26995 | 0.5513 | 529 | 0.0018904 | 17.9543 | 142.8036 | 1042.155 | L 1-6
7 | 8 | 345 | 100 | 600 | 0.06786 | 0.53988 | 1.1026 | 1190.25 | 0.00084016 | 80.7704 | 642.5922 | 926.3768 | L 1-2

## Load Data
Load Data
Name | Terminal Bus | Active Power (MVA) | Reactive Power (MVAR) | Power Factor
L1 | Bus 1 | 300 | 186 | 0.85
L2 | Bus 2 | 250 | 121 | 0.9
L3 | Bus 3 | 350 | 115 | 0.95
L4 | Bus 4 | 300 | 186 | 0.85
L5 | Bus 5 | 100 | 48 | 0.9
L6 | Bus 6 | 150 | 49 | 0.95
Shunt Data
Name | Terminal Bus | Active Power (MVA) | Reactive Power (MVAR)
S1 | Bus 4 | - | 200
S2 | Bus 5 | - | 40
S3 | Bus 7 | - | -100

## Generator Data
Generator Data
Name | Terminal Bus | Nominal Apparent Power (MVA) | Nominal Voltage (KV) | Power Factor | Active Power (MW) | Voltage (pu)
G1 | Bus 9 | 750 | 15.5 | 0.8 | 0 | 1
G2 | Bus 10 | 640 | 15 | 0.8 | 400 | 1.01
G3 | Bus 11 | 384 | 18 | 0.8 | 270 | 1.01
G4 | Bus 12 | 474 | 13.8 | 0.8 | 330 | 1.01

## Transformer Data
Transformer Data
Name | From Bus | To Bus | Type | MVA Capacity | Uk (%) | Vector Group
T1 | 1 | 7 | Autotransformer | 500 | 13 | YNyN
T2 | 1 | 9 | Step-up | 800 | 12 | YNd11
T3 | 2 | 10 | Step-up | 700 | 12 | YNd11
T4 | 3 | 8 | Autotransformer | 500 | 13 | YNyN
T5 | 3 | 11 | Step-up | 400 | 10 | YNd11
T6 | 6 | 12 | Step-up | 500 | 11 | YNd11

## Bus Data
Bus Data
Bus Name | Nominal Voltage (kV) | Type | Pgen (pu) | Pload (pu) | Qload (pu) | Bshunt (pu) | Vmag (pu)
1 | 230 | PQ | - | 3 | 1.86 | - | -
2 | 230 | PQ | - | 2.5 | 1.21 | - | -
3 | 230 | PQ | - | 3.5 | 1.15 | - | -
4 | 230 | PQ | - | 3 | 1.86 | 2 | -
5 | 230 | PQ | - | 1 | 0.48 | 0.4 | -
6 | 230 | PQ | - | 1.5 | 0.49 | - | -
7 | 345 | PQ | - | - | - | -1 | -
8 | 345 | PQ | - | - | - | - | -
9 | 15.5 | SL | - | - | - | - | 1
10 | 15 | PV | 4 | - | - | - | 1.01
11 | 18 | PV | 2.7 | - | - | - | 1.01
12 | 13.8 | PV | 3.3 | - | - | - | 1.01

## Validation
Validating the load flow sloution
| Value[1] |  | PF Values |  | Errors
Bus | Voltage Magnitude (pu) | Voltage Degrees | Voltage Magnitude (pu) | Voltage Degrees | Absolute Error (Voltage) | Absolute Error (Degrees) | Relative Error (Voltage) | Relative Error (Degrees)
1 | 0.98 | -4.2 | 0.96416 | -34.5136 | 0.015838 | 30.3136 | 0.016161 | -7.2175
2 | 0.99 | -3 | 0.97682 | -35.8556 | 0.013182 | 32.8556 | 0.013315 | -10.9519
3 | 0.99 | -30 | 0.94979 | -86.3108 | 0.040208 | 56.3108 | 0.040614 | -1.877
4 | 0.99 | -30.6 | 0.90175 | -86.9489 | 0.088255 | 56.3489 | 0.089146 | -1.8415
5 | 0.99 | -30.6 | 0.84528 | -80.8403 | 0.14472 | 50.2403 | 0.14619 | -1.6418
6 | 1 | -4 | 0.9842 | -43.9625 | 0.015804 | 39.9625 | 0.015804 | -9.9906
7 | 1 | -7.2 | 0.94208 | -36.5943 | 0.057918 | 29.3943 | 0.057918 | -4.0825
8 | 1.03 | -26.6 | 0.94388 | -84.4254 | 0.086119 | 57.8254 | 0.083611 | -2.1739

## Voltage Dependency
Voltage Dependence of the loads
| Exponential Coefficient | Generation (MW) | Generation (MVAR) | Load (MW) | Load (MVAR) | Total MW Losses | Total MVAR Losses
Case I: Constant Impedence | 2 | 1406.064 | 613.1841 | 1369.613 | 687 | 36.4507 | 54.534
Case II: Constant Current | 1 | 1440.417 | 672.6568 | 1399.169 | 687 | 41.2481 | 107.5181
Case III: Constant Power | 0 | 1505.84 | 851.5531 | 1450 | 687 | 55.8397 | 267.01